## Pre-Bid Questions Log
Q# | Date Received | Bidder/Company | Contact Name | Spec Section / Drawing Ref | Discipline | Question | Assigned To | Final Response
| 2026-04-28 | Grounded Electric | n/a |  | Owner | No security or A/V drawings. Will need wires pulled and sound system in Gym and PA. | Owner | Owner will solicit proposals and hold contract directly
| 2026-05-06 | Daniels | Joe Trainer | I210 | Architectural | The B-2 base is called out as 44x22 size on the material schedule on I210. My assumption is this will be a cut base tile from the T-1 24x24 tile. What trim will cap this base? | Iconica | It should have read 4x24. The cap is listed in the B-2 box on the Finish Schedule
| 2026-05-06 | Daniels | Joe Trainer | I210 | Architectural | The TR-2 and TR-3 trims for the wall tile will not work at the top of T-2 tile or where the wall tiles end at a corner. This is only for where a tile will continue around corners. Should all of these trims maybe be switched to the Jolly trims? | Iconica | TR-4 has been added to the schedule for the top of a tiled wall that does not go to the ceiling. TR-2, etc. was never intended for inside corners - only outside corners.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | What restrictions apply to noise, vibration, dust, and parking during construction? | MSCR | Maintain access to primary parking & access in front and rear of current facility (7333), coordinate all work on existing facility & opening connection points based on program schedules/facility needs, dust and noise mitigation when facilities are opened.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Will phasing be required for the parking lot improvements? | MMSD | Improvements will either need to ensure there is parking available at 7333 W Towne Way or coordinate scheduling during breaks in the program calendar.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | What hours of work are permitted given the mall environment? Is overnight or weekend work expected or restricted? | MSCR | Contractors must adhere to City of Madison Construction Noise Control Regulations and Ordinances.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Are there CBL-imposed work-hour restrictions, parking-lot closure restrictions, or noise restrictions specific to mall operations? | MSCR | We are not aware of any. This is not a CBL property
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Are there owner-furnished items (in particular - gym scoreboards, dehumidification unit, pool equipment, signage) that the contractor coordinates but does not buy? | Iconica | All OFCI items as noted on plans. No gym scoreboards in project. Yes, OFCI for pool equipment. Signage is by owner. Dehumidification unit is by mechanical contractor per plans.
| 2026-05-08 | Ideal | Zach Krause | A461 | Architectural | Please confirm if the ceiling mounted interactive project is CFCI, OFOI, or OFCI noted on A641 | Iconica | Added note to drawings.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Please confirm that the netting, upholstery & peg board is all CFCI | Iconica | CFCI.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Confirm the deduct-alternate and add-alternate schedule. The cover sheet lists PL01, PL02, P01, M01, M02, E01 — please confirm bid response format and any additional alternates as there is no line item to put in the bid form. | Iconica | Bid form to be updated.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Are there DBE / MBE / WBE participation goals or apprenticeship utilization requirements? Please also confirm there are no Best Value Contracting (BVC) requirements for this project. | MSCR | Per MMSD BOE Policy 5000: Extra consideration may be given to contractors that have actively employed apprectices over the past two years and engage sub-contractors that qualify as historically underutilized businesses
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Is the Madison building permit secured by the Owner, or does the GC pay for the building permit along with subcontractor's paying their respective permit? | Iconica | GC and subcontractors to pay for all building permits
| 2026-05-08 | Ideal | Zach Krause |  | WTI | Has the Wisconsin DSPS public-pool design submission been reviewed and approved? What's the status? | Iconica | This pool's plans have been submitted to WI DSPS (ref. Public Swimming Pools Plan Review DIS-042616838). Scheduled Review Date: 10JUN2026
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Is there a contingency or owner-controlled allowance line on the bid form? | MSCR | Not bid form, we are holding that seperately
| 2026-05-08 | Ideal | Zach Krause |  | Structural | Is there anticipated structural changes required after field verification is completed by steel erectors? | Iconica | We are not expecting any changes, however there will likely be reinforcement required at the joists supporting the skylights
| 2026-05-08 | Ideal | Zach Krause |  | Structural | Does Iconica (SEOR) provide a recommended shoring sequence for the column removals, or is the shoring scheme entirely the contractor's design responsibility? Will there need to be a required stamped submittal on this if by the contractor? | Iconica | This is the contractors responsibility, stamped submittal required
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Is the existing ballasted EPDM roof being patched only at new openings, or is a full roof replacement / overlay anticipated as a landlord-coordinated scope rider? | Iconica | Only patched at new openings.
| 2026-05-08 | Ideal | Zach Krause | S101 | Structural | S101 shows 7 existing footings being removed and replaced (keynote 1) but 8 columns being removed (keynote 2). Confirm whether one column foundation is reused / abandoned in place or whether this is a drafting count discrepancy. | Iconica | There are 10 new footings; 3 are under new columns, 7 are under existing columns that are being reinforced due to additional loading. There are 8 columns being removed, the footings are being abandoned, they could be removed or left.
| 2026-05-08 | Ideal | Zach Krause | S202 | Structural | S202 Note 6 estimates existing roof deck at 1-1/2" 20 gauge while the new spec calls for 1-1/2" 22 gauge. Confirm transition / fastening / continuity detail at deck mismatch seams. | Iconica | We have updated the sheets to show new deck to match existing deck
| 2026-05-08 | Ideal | Zach Krause |  | Structural | Has the Owner or A/E conducted any prior survey of existing column wall thicknesses, or is full field-verification of every reinforced column the contractor's discovery cost? | Iconica | SSD has done a prior survey of exisitng steel wall column thicknesses at a single column, the contractor will need to confirm wall thickness at each column that is being reinforced
| 2026-05-08 | Ideal | Zach Krause |  | WTI | Confirm pool start-up, water-balance, and operations-training scope and timing relative to substantial completion. | Iconica | Prior to substantial completion
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Confirm electrical service size — new service or extension of existing? What amperage and voltage? | Iconica | Existing 600A 480/277V 3-phase service will be re-used, unless any alternates are accepted. If any alternates are accepted new service will be required at size of 800A 480/277V, 3-phase
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Is generator backup required? If so, please clarify scope and equipment. | Iconica | No, there will be an inverter as specified on E701 EMERGENCY POWER INVERTER SCHEDULE.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Confirm fire-alarm panel — new or tie into existing 7333 system? | Iconica | New Honeywell/Notifier fire alarm system completely separate to existing building
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Confirm sprinkler design density for the natatorium- are humidity-tolerant fittings required? | Iconica | Fire Protection is design build by contractor, hazards and densities shall comply with code. All piping/fittings is above ceilings and ok as specified. Sprinkler heads shall be corrosion resistant for pool and pool service rooms. Those rooms include Lockers, Janitor, Pool Mechanical, Pool Storage, Chlorine, Muriatic Acid, and Pool Storage.
| 2026-05-08 | Ideal | Zach Krause |  | Civil | Please confirm site disturbance area and stormwater management requirements for parking lot resurfacing. | Iconica | The project will require an erosion control permit. Stormwater management is not required.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Please confirm construction staging area and approved truck-delivery routes. | MSCR | The rear parking lot is acceptable for a staging area so long as the fire lane is maintained.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Is utility upsizing (water, gas, sanitary, electrical) required to support the natatorium loads? If so, by whom? Is CBL providing or coordinating any utility upsizing (water service, sanitary, electrical, gas) to support the natatorium load? | Iconica | Gas service does not need to be upsized. MGE has confirmed that the existing meter setup is acceptable. Sanitary/Water sizes are adequate. New Storm added for pool backwash and approved by City of Madison Engineering. Refer to Line item 24 asking about electrical service sizing.
| 2026-05-08 | Ideal | Zach Krause | 01 73 10 | Structural | What is the anticipated review-cycle turnaround for cutting/patching submittals (per Spec § 01 73 10, 10-day lead) on each of the column-removal events? | Iconica | The owner will be responsible for engaging any special inspection agencies
| 2026-05-08 | Ideal | Zach Krause |  | Structural | What is the structural review path for the deferred framing submittal (RTU support framing, joist reinforcement at point loads, openings)? | Iconica | This is in SSD's scope
| 2026-05-08 | Ideal | Zach Krause |  | Structural | Confirm whether the existing roof deck transition (existing 20 gauge to new 22 gauge) requires any specific flashing or fastener detail beyond generic spec. | Iconica | New deck will be 20 guage to match existing, if the new deck does not mesh well with existing, then we will remove existing from support to support and replace it with new
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Has Iconica engaged with CBL Properties regarding the structural intervention, or is CBL coordination the contractor's responsibility post-award? | MSCR | This is not a CBL property. MMSD owns the building
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | What survey or condition-assessment information of the existing building does Iconica have on file that can be shared with bidders? Or is everything shared already? | Iconica | Everything is shared already
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Who is responsible for coordinating special inspections? Owner? Has MMSD pre-engaged a special-inspection agency as required per new IBC 2021 code? | MMSD | Owner will solicit proposals and hold contract directly
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Will WTI act as commissioning agent (Cx) for the pool MEP package, or is Cx contracted separately? | MMSD | Separately
| 2026-05-08 | Ideal | Zach Krause |  | WTI | Confirm Alternate PL02 — pool heater heat pump system. Is the heat pump base scope or alternate? Equipment specifications and weights for pool heat pump (WHP) and pool heat pump pump (HPP) family — WHP-1, 2, 3 and HPP-1, 2, 3. | Iconica | The air-source heat pumps (ref. Sheet PL401 - H2A, H3A, and H4A) are an owner-requested add-alternate. Units scheduled: Hydro Royal HR150TA (www.hydroroyal.com/model-150-heat-and-cool.html) Note the H1A base heater will be required with or with-out the alternate heat pumps included.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Confirm Alternate M01 — pool water condenser energy recovery from PDU-1. If accepted, what is the additional pump (P-1), hydronic piping, and heat trace scope? | Iconica | See additional scope on drawings M201 & M901 as well as related specifications sections. Heat trace scope is defined on drawing E201P.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | What CBL-required approvals must be obtained before structural work begins in the leased space? | MSCR | This is not a CBL property. MMSD owns the building
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | The Bradley items, Lockers and compartments- The specs are mentioning details/material types the manufacturer does not offer. For example, the phenolic material is only black core and not color thru the and the fire rating is only B and A. Please advise how you want us to proceed. | Iconica | The Bradley selections are correct and we will strive to align the spec with the product selection.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Confirm dehumidification unit manufacturer and model as specifications do not appear to specify | Iconica | Drawing M701, POOL DEHUMIDIFICTION UNIT SCHEDULE identifies the basis of design manufacturer and model. Specification SECTION 238416.13-2.1-A lists three acceptable manufacturers.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Is the natatorium HVAC on an independent system, or tied into existing facility air? | Iconica | The pool dehumidification unit is independent of other systems. See drawings M201 and M901.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Can you please confirm the preferred (if any) HVAC control vendor for this project and if you have contact info? | Iconica | See drawing M001, GENERAL NOTE #28.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Please confirm acceptable RTU manufacturers and models, if applicable. Are all new RTUs to be contractor furnished and installed? | Iconica | See equipment schedules on drawing M701 for basis of design manufacturers and models. See respective specification sections for list of additional acceptable manufacturers.
| 2026-05-08 | Ideal | Zach Krause |  | MEP | Is the heat reclaim from pool water system specified as base scope, alternate (Alternate M01), or owner option? | Iconica | Drawing M701, POOL DEHUMIDIFICTION UNIT SCHEDULE note #12, the pool water heat reclaim is part of the base bid. Alternate #M01 is for the removal of that option.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Please confirm no ADA automatic door operators are required | Iconica | No ADA automatic door operators.
| 2026-05-08 | Ideal | Zach Krause | A801 | Architectural | On A801, it notes “G.C. TO VERIFY STRUCTURAL CAPACITY OF EXISTING JOISTS FOR NEW BASKETBALL GOAL AND PROVIDE ALLOWANCE FOR STRUCTURAL REINFORCEMENT”. Where do we note this allowance in the bid form if this is required, or what is the allowance we should carry? If this is just for the drops/bridges, typically the vendor provides enough top structure in place so it is not required, but ultimately the structural engineer of record should dictate what is required depending on the weight-bearing loads or provide an allowance we should carry. | Iconica | Note revised in addendum drawings.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Are there any soil reports or boring logs available? | MSCR | No
| 2026-05-08 | Ideal | Zach Krause | 3-A463 | Architectural | Please provide a spec for the netting shown on 3-A643. Should this be included in spec section 116623 or others? | Iconica | Provide netting called out as basis of design on 3/A643
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Lockers manufactures a full range of locker types and can match any specifications outlined in the project manual, including materials, construction methods, dimensions, configurations, and design requirements. LockersMFG manufactures in the USA. Attached an equivalency/substitution request for LockersMFG to be on the list of preapproved manufacturers so the project team has the information they need. Can you confirm if this is an approved substitute? | Iconica | We are not accepting any substitutions at this time.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Please confirm if the both the mural design AND installation is CFCI? Or is just the mural install only CFCI? | Iconica | CFCI. Contractor to hire designer listed in bid docs - no exceptions.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | Does the gymnasium have a scoreboard or shot clock? If so, is that CFCI? | Iconica | No scoreboard or shot clock.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | There is no spec section for the window coverings – please confirm this is CFCI | Iconica | CFCI.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | There is no spec section for signage. Aside from murals, is the restroom ADA signage the only CFCI signage? | Iconica | All signage by owner.
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | We are unable to locate any material or fence specifications. Are there specific materials you would like us to base our pricing on, or should we assume standard fence materials? There is also a callout for privacy slats, but I could not find any specifications regarding the color, style, or percentage of privacy required. | Iconica | See addedum drawings for fence detail
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | The Laminated Glass for Frames D, H & J is too large for fabrication per Cardinal, Oldcastle and Trulite. Could the A/E consider a smaller diameter at these areas or utilize a different type/thickness of glass since our glazing vendors are saying that it is too large to be made? Perhaps the A/E could work with an Oldcastle or Cardinal rep. Attached | Iconica | See addendum drawings.
| 2026-05-08 | Ideal | Zach Krause |  | Owner | Also, for the Salto door hardware, all of our vendors are stating that this cannot be contractor furnished and needs to be procured by the owner directly. | MMSD | OFOI
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | For textures, do we need to apply that or all walls or ceiling? If not, can you clarify where? | Iconica | With the exception of the areas receiving murals and wall coverings, all walls receive a texture that matches what was done in the adjoining MSCR space.
| 2026-05-08 | Ideal | Zach Krause | A700 | Architectural | On Sheet A700 general note 7, do you not need acoustical sealant at the top of walls? | Iconica | Not needed at top of wall
| 2026-05-08 | Ideal | Zach Krause | 3-A512 & 2-A401 | Architectural | On detail 3-A512 and also 2-A401, can you confirm if the pool drywall goes to deck all the way? What about insulation? | Iconica | Drywall and insulation to run to height of drywall ceiling in pool. Area above pool to remain open to promote air movement
| 2026-05-08 | Ideal | Zach Krause |  | Architectural | For WC-1 & WC-2, The manufacturer requirements show level 4 or 5 as acceptable. Please confirm level 4 is OK. | Iconica | Level 5 is required for all walls receiving wall covering. The wall is also required to be clean and free of any debris prior to wall covering installation.
| 2026-05-08 | Ideal | Zach Krause | A643 | Architectural | Can you provide a detail on the stairs for A643 and how it is constructed? | Iconica | Stairs shown on 3/A643 are constructed of cold formed metal framing, fire retardant plywood sheathing, and floor finish.
| 2026-05-08 | Ideal | Zach Krause | 3-A641 | Architectural | Can you provide a detail of the reflected ceiling plan for the play 112 area ceiling? 3-A641 appears to just show the first tier ceiling plan, what about second? | Iconica | See second floor Play 112B on 1/A801.
| 2026-05-08 | Vogel | Nick Schuch | 00 43 80 | Owner | Page 21 of project manual states to "reference Section 00 43 80 - Affirmative Action/Equal Employment Opportunity Requirements: The information requested in this Section shall be submitted with the bid, as necessary". No section 00 43 80 was provided. We have 00 43 75, and 00 50 00. | MSCR | Required AA/EEO Forms found in Appendices A, B and C near the end of the RFP. Section 00 43 80 is not included and not required.
| 2026-05-08 | Vogel | Nick Schuch | AD201 | Owner | Please confirm all existing store fixtures will be removed prior to start of work as they are not shown on sheet AD201. | MSCR | If not removed by Office Max, MMSD will remove.
| 2026-05-08 | Vogel | Nick Schuch | AD201 | Owner | Please confirm all checkout stations and stands will be removed prior to start of work as these are not shown on sheet AD201. | MSCR | If not removed by Office Max, MMSD will remove.
| 2026-05-08 | Vogel | Nick Schuch | AD201 | Owner | Please confirm all existing casework at reception, customer support, etc. will be removed prior to start as these are not shown on sheet AD201. | MSCR | If not removed by Office Max, MMSD will remove.
| 2026-05-08 | Vogel | Nick Schuch | AD201 | Owner | Please confirm all storage racking in back warehouse will be removed prior to start of work as these are not shown on sheet AD201. | MSCR | If not removed by Office Max, MMSD will remove.
| 2026-05-08 | Vogel | Nick Schuch |  | Structural | With the added weight of the new skylights shown on the structural drawings. Should any new steel framing be required to support these? If so, please confirm sizes and connection details. | Iconica | Yes, see sheet S801 for cold formed framing of skylights. Reinforcement of existing joists, if required, is still TBD
| 2026-05-08 | Vogel | Nick Schuch | S101 | Structural | ON sheet S101, new top of footing elevation is called out to be 97’-9 ½”. New top of slab is 98’. The new slab is 5” thick. Top of footing will be covered by the slab by 1” and the typical detail 9/S301 doesn’t appear to be accurate. Please clarify. | Iconica | This has been updated, see drawings. Footing is now 9" thick
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Existing storefront has a sliding security gate. Please confirm what should be done with this. | Iconica | Demo sliding security gate.
| 2026-05-08 | Vogel | Nick Schuch |  | Owner | Cover sheet calls for a variety of different alternates but these are not on the bid form. Please confirm. | Iconica | Added to Bid Form
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Please confirm what should be done at exterior wall where moisture appears to be coming through the wall. Attached | Iconica | IMAGE
| 2026-05-08 | Vogel | Nick Schuch | 6/A513 | Architectural | Detail 6/A513, has a new frame going into existing 12" CMU. Is that CMU grouted solid or does it need to be grouted for the detail to work? | Iconica | Conditions will need to be verified. If cores are not already grouted solid they will need to be for new door opening
| 2026-05-08 | Vogel | Nick Schuch | A801 | Architectural | Drawing A801 indicates Sound Baffles to hang from aircraft cables at 20'8" AFF. The RG-3 and DuctSox will be below that at 17'5" is there any concern with airflow from the DuctSox will cause the baffles to swing? | Iconica | No concerns.
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Please confirm what should be done with the bollards that are located at the traffic doors to the back warehouse as they are not shown on the demo drawings. Attached | Iconica | Demo bollards.
| 2026-05-08 | Vogel | Nick Schuch |  | Structural | Please provide roof loading requirements (Dead load, Live load, etc.) for temporary shoring for new beams installed at existing joist locations | Iconica | See sheet S001 for design loads
| 2026-05-08 | Vogel | Nick Schuch | AD203 | Architectural | Please provide as-built conditions for demolition of the Entry Marquee called out on AD203. If no as-builts are available, please confirm assumed condition to allow for pricing. | Iconica | No as-builts are available. Contractors to make assumtion based on site visit
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Please provide specification or density required for geofoam at the pool viewing room. | Iconica | Use a EPS Type II Geoform 1.5lb/ft^3. Contractors can also use fill from pool excavations if existing soils material is acceptable
| 2026-05-08 | Vogel | Nick Schuch | A302 & A303 | Architectural | Drawings A302 and A303 indicate an exterior Pipe Stair Hand and Guardrail does not have a connection detail. The only connection detail for handrails is on 6 PL101 which appears to be specific to the pool. Please confirm. | Iconica | Surface mounted base plates for guardrail posts. Handrail wall mounted brackets fastened to existing masonry wall with appropriate masonry fasteners per manufacturers recommendations.
| 2026-05-08 | Vogel | Nick Schuch | A801 | Structural | Drawing A801 indicates G.C. to verify structural capacity of existing joists for new equipment and to provide an allowance for structural reinforcement. Can the Structural Engineer of record please confirm what modifications need to be made as part of this allowance? | Iconica | Note has been updated, SSD (structural) will take care of analysis of joist
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Doors 142 and 141 are marked on the door schedule as existing. Doors 141 and 142 are in new walls and cannot be existing. Please confirm door and frame type needed. | Iconica | Doors 141 and 142 are existing to be reused doors from the existing storage room that will be demolished to create Corridor 101.
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Exterior door in room 125 is not called out. Please provide callout and update schedule. | Iconica | Existing exterior door in Pool Mech. 125 to remain as is.
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | Group 16 Hardware listed on opening 143. No Hardware group 16 is present on schedule please confirm hardware | Iconica | Hardware group added per addendum drawings
| 2026-05-08 | Vogel | Nick Schuch | A711 | Architectural | Page A711 Door Hardware General Notes states "All door hardware to be provided by MMSD" and "General contractor to install all door frames, install hinges and set doors MMSD to install all other remaining hardware" A/E Please confirm contractors to only supply and install frames and mount doors on frames. MMSD to supply and install for Kickplates, closers, Salto systems wall stops, ADA pulls, dead bolts, armor plates, flush bolts, astragals, thresholds, dust proof strikes, overhead stops, card readers, electric strikes, push pulls, mag hold opens. | Iconica | Yes
| 2026-05-08 | Vogel | Nick Schuch |  | Architectural | A/E to confirm note 4 on Door schedule openings 122B, 123, 125A, 125B, 131, 132. no door hardware note 4 is present | Iconica | Note 4 added in addendum - See addendum plans
| 2026-05-08 | Vogel | Nick Schuch | A201 | Architectural | On floor plan A201, Gridlines H.6 and 8, at the plan southeast corner of the gym to the left as you enter the lounge 109 corridor, there is a wing wall near the reception desk that is not called out on the plan. Backup wall type is 9C, no elevation is provided to detail this item. It appears to be a display board or architectural casework. | Iconica | See elevation 5/A638 for wall profile. Wall type tag added to 1/A639.
| 2026-05-08 | Vogel | Nick Schuch | 1/A641 | Architectural | Detail 1/A641 First Flr. of Play 112A notes the base to be B-2 is this correct as this is a tile product? | Iconica | It should have read B-1 and not B-2.
| 2026-05-08 | Vogel | Nick Schuch | E100 & C002 & C100 | Electrical/Civil | Drawing E100 indicates a Proposed New Pole S1 Plan South of Vestibule 179 in the parking lot. The Civil Drawing s such as C002 and C100 do not indicate any asphalt repair for that trench. Please confirm the conduit path for pricing and repair work needed. | Iconica | Direct bore from island. Drawings will be updated to reflect this direction.
| 2026-05-08 | Vogel | Nick Schuch | E201L | Electrical | Drawing E201L note E25 indicates 30' of RGB skylights, however in the drawing it indicates 25' at the two round skylights. Please confirm which is correct. | Iconica | 25' is correct. This will be updated as part of addendum #1 drawing
| 2026-05-08 | Vogel | Nick Schuch | E501 | Owner | Confirm card access wiring and devices are by owners’ access control vendor and we are only providing rough-ins and required raceways. E501- #6 & #10 note #5. | MSCR | Raceway and cabling for wired equipment. Final terminations an Cx will be done by MMSD. We can add some plan notes or something for what is needed where.
| 2026-05-08 | Vogel | Nick Schuch |  | Owner | What is the required fire alarm system we should be providing? Should we plan on tying into the existing system or providing a new system? | MSCR | Provide a new Honeywell/Notifier system. The new and existing building are divided by fire rated wall, so separate fire alarm systems.
| 2026-05-08 | Vogel | Nick Schuch | E001 | Owner | Who is responsible for providing cameras? E001 security symbol schedule shows camera RI only by contractor. If that’s not the intent and the contractor should be providing cameras, please identify types and any head-end storage requirements we should also be adding. | MSCR | Contractor will provide cameras. I will follow up with what should be provided. No head end storage needed, they live on the network servers.
| 2026-05-08 | Vogel | Nick Schuch |  | Owner | What manufacturers of structured cabling will be accepted? | MSCR | CommScope Technologies for cabling. Panduit for jacks, faceplates, patch panels.
| 2026-05-08 | Vogel | Nick Schuch |  | Owner | Confirm structured cable type - CAT6 plenum for cameras and workstation outlets. CAT6A for WAP(s)? | MSCR | Correct
| 2026-05-08 | Vogel | Nick Schuch |  | Owner | WAP(s) – Please confirm these are owner furnished contractor installed. | MSCR | Owner furnished, owner installed
| 2026-05-08 | Vogel | Nick Schuch |  | Electrical | Confirm quantity of CAT6A cables at each WAP. (1) or (2) CAT6A each? | Iconica | (1) CAT6A
| 2026-05-08 | Vogel | Nick Schuch | E701 | Owner | Confirm only copper wiring is allowed as shown in specification and E701. | MSCR | A. The basis of design is copper conductors. Contractor is responsible for selecting the aluminum conductor size(s) as needed to match the ampacity of the copper conductors. Contractor to submit documentation showing the conversion from copper to aluminum, including conduit sizes. Include a cut sheet of the proposed aluminum conductor that shows conductor dimensions (outside diameter or overall square inch area). B. Feeders: Aluminum, AA-8000 series alloy, compact stranded conductor, 600-volt insulation, USE-2/RHH/RHW-2 or XHHW-2. C. Feeders in Underground Conduit: Aluminum, AA-8000 series alloy, compact stranded conductor, 600-volt insulation, USE-2/RHH/RHW-2. D. Aluminum conductors shall be terminated with compression lugs, copper plated terminal pins, or manufacturer approved method. Apply anti-oxidation paste. Torque test conductor connections and terminations to manufacturer's recommended values. E. Aluminum conductors shall NOT be allowed for the following: 1. Elevator equipment. 2. Feeders rated less than 100 amps. 3. Motor feeders and branch circuits. 4. When prohibited by the manufacturer of the equipment. 5. Grounding and Bonding. 100- Above 4' EMT is acceptable. IMC is also acceptable below 4'
| 2026-05-08 | Vogel | Nick Schuch | 26 0533-3 | Electrical | It is called out in the spec Raceways and Boxes for Electrical Systems 26 0533-3 to be rigid metal conduit in the mechanical rooms. Since the panels sit in the mechanical room, I am requesting clarification on if all raceway in the mechanical room needs to be rigid metal or if it is acceptable to be standard EMT above a certain height? | Iconica | It is acceptable to transition to EMT above 10' in the mechanical room
| 2026-05-08 | Vogel | Nick Schuch | L100 | Civil | Drawing L100 indicates 4 Inches wood mulch. However on the east side of the parking lot limits to the extents of what should be covered are not identified. Please clarify. | Iconica | Trees on the east side of the parking lot are all individual trees in lawn. Each individual tree to receive a 4' mulch ring with a mulch depth of 4".
| 2026-05-08 | Vogel | Nick Schuch | M701 | MEP | Drawing M701 – Alternates called out on schedules but I don’t see alternates on the bid form or an alternates spec section. Please advise. Attached (3) | Iconica | Bid form by MMSD/MSCR. PDU-1 & P-1: Alternate is for removal pool water energy recovery and associated components. There is nothing additional to specify. DOAS-1, RTU-1, RTU-2, & RTU-3: Equipment schedules will be updated in an addendum to include basis of design model and manufacture with performance data of alternate equipment.
| 2026-05-08 | Vogel | Nick Schuch | 99000-13 | Architectural | Spec 99000-13 Painting - Please clarify Section I - Gypsum Board Section 2 - Finish: (There appears to be redundancy with the various types of paint to be used and noted 3 times "All ceilings shall have a flat paint finish". Sheet I210 - Finish Schedule notes the paint to be Benjamin Moore Scuff-X for all the paints P1-P8 to be used. Please clarify which paint is to be used where. | Iconica | Benjamin Moore Scruff-X is not required on the ceiling

## Addendum Tracker
Addendum # | Issue Date | Questions Included | Drawing Revisions | Spec Revisions | Issued By | Notes